## Guide
Residential Lighting Estimation – Calculation Workbook
University of Duhok – Electrical & Computer Engineering – Estimation course (4th year) – Valina Hani
How to use
1 | Change values only in BLUE cells (inputs). Black cells are formulas – do not overwrite them.
2 | Cells with YELLOW fill are assumptions or estimates (prices, cable lengths, quantities): replace them with real values.
3 | Inputs sheet: ceiling height, lamp data, maintenance factor, voltage, and the utilization-factor row from Table 2.
4 | Rooms sheet: enter length, width, target lux and circuit for each room. Lamps, power and current are calculated automatically.
5 | To add a room, insert a row inside the table (above the Total row) and copy the formulas from the row above.
6 | Circuits sheet: lamps per circuit, MCB, cable capacity and voltage-drop checks. Cost sheet: bill of quantities and total cost.
Colour code
Blue text | Input (hard-coded value)
Black text | Formula
Green text | Link to another sheet
Yellow fill | Assumption / estimate to be verified
Method
Room index | k = (L × W) / (Hm × (L + W)), Hm = ceiling height − work-plane height
Utilization factor | UF interpolated linearly from Table 2 (C = 0.7, W = 0.5, F = 0.3); if k < 0.75 the lowest value is used
Number of lamps | n = (A × E) / (F × UF × MF), rounded up to a whole number (a manual override is allowed)
Check | E achieved = n × F × UF × MF / A must be ≥ target E (the check column shows OK or CHECK)
Current | I = P / V (power factor taken as 1)
Voltage drop | ΔV = 2 × ρ × L × I / Ac, ρ = 0.0225 Ω·mm²/m (copper at 70 °C), limit 3 % for lighting
Sources and assumptions
Lux levels | Table 1 of the project report. Sport room (400 lx) is not in Table 1 – assumed equal to Study / Office.
Lamp | 20 W, 2500 lm, MF = 0.8 (project data). Supply 230 V, 50 Hz (assumed).
Cable capacity | 1.5 mm² copper PVC: lowest value in Table 3 (13 A) used as Iz (conservative).
Prices, lengths | Unit prices are assumed market prices in USD; cable / conduit lengths are estimates from the plan (±10 %).

## Inputs
Inputs
Blue = input. Source: project data and report tables.
Parameter | Value | Unit | Note
Ceiling height | 3 | m | From the plan
Work-plane height | 0.8 | m | Standard work-plane height
Mounting height Hm | 2.2 | m | Ceiling height − work plane
Lamp power | 20 | W | Project data
Lamp luminous flux F | 2500 | lm | Project data
Maintenance factor MF | 0.8 |  | Project data
Supply voltage V | 230 | V | Assumed single-phase supply
Copper resistivity ρ | 0.0225 | Ω·mm²/m | Copper at 70 °C
Max voltage drop (lighting) | 3% |  | 3 % limit usually applied to lighting circuits
Lamp price | 2 | $ | Price used in the original report
Table 2 – utilization factor row used (C = 0.7, W = 0.5, F = 0.3)
Room index k | 0.75 | 1 | 1.25 | 1.5 | 2
UF | 0.69 | 0.75 | 0.8 | 0.84 | 0.89
Table 1 – recommended illuminance (reference)
Room | Min (lx) | Max (lx)
Living Room | 150 | 300
Kitchen | 200 | 400
Dining Room | 150 | 250
Bedroom | 150 | 200
Bathroom | 200 | 300
Hallway | 100 | 150
Staircase | 150 | 150
Study / Office | 400 | 500
Storage Room | 100 | 150

## Rooms
Room-by-room lighting calculation (lumen method)
Enter L, W, target E and circuit in blue cells. Green = linked from Inputs.
Room | Circuit | Length L (m) | Width W (m) | Target E (lx) | Area A (m²) | Room index k | UF | n calculated | Manual override (lamps) | n adopted | E achieved (lx) | Power (W) | Current (A) | Lamp cost ($) | Illuminance check
Bedroom 1 | L1 | 4.5 | 3.8 | 150 | 17.1 | 0.93647 | 0.73 | 1.7568 |  | 2 | 170.7602 | 40 | 0.17391 | 4 | OK
Bedroom 2 | L1 | 4.5 | 3.8 | 150 | 17.1 | 0.93647 | 0.73 | 1.7568 |  | 2 | 170.7602 | 40 | 0.17391 | 4 | OK
Bedroom 3 | L1 | 4.5 | 3.8 | 150 | 17.1 | 0.93647 | 0.73 | 1.7568 |  | 2 | 170.7602 | 40 | 0.17391 | 4 | OK
Bathroom 1 | L2 | 2.9 | 2 | 200 | 5.8 | 0.53803 | 0.69 | 0.84058 |  | 1 | 237.931 | 20 | 0.086957 | 2 | OK
Bathroom 2 | L2 | 2.9 | 2 | 200 | 5.8 | 0.53803 | 0.69 | 0.84058 |  | 1 | 237.931 | 20 | 0.086957 | 2 | OK
Dressing Room | L2 | 2.9 | 2 | 200 | 5.8 | 0.53803 | 0.69 | 0.84058 |  | 1 | 237.931 | 20 | 0.086957 | 2 | OK
Entrance | L2 | 2.9 | 2 | 200 | 5.8 | 0.53803 | 0.69 | 0.84058 |  | 1 | 237.931 | 20 | 0.086957 | 2 | OK
Sport Room | L2 | 4.5 | 2.3 | 400 | 10.35 | 0.69184 | 0.69 | 3 | 4 | 4 | 533.3333 | 80 | 0.34783 | 8 | OK
Living Room with Open Kitchen | L3 | 9.6 | 5.3 | 300 | 50.88 | 1.5522 | 0.85 | 8.9788 |  | 9 | 300.7075 | 180 | 0.78261 | 18 | OK
Total | [9 empty] | 23 |  | 460 | 2 | 46
Notes: dressing room is 2.35 × 2.9 m on the plan (k = 0.59, UF = 0.69, n = 0.99 → 1 lamp), same result as the grouped 2.9 × 2.0 m; for k below 0.75 the lowest tabulated UF (0.69) is used.
Note on E12: Sport room is not listed in Table 1; 400 lx assumed (Study / Office value).
Note on J12: Calculated n = 3.0 (minimum). 4 lamps adopted for a symmetrical 2 x 2 layout. Delete this value to use the calculated number.

## Circuits
Lighting circuits, protection and voltage drop
Lamps and power are summed from the Rooms sheet by circuit name.
Circuit | Area supplied | Lamps | Power (W) | Current Ib (A) | MCB In (A) | Cable size Ac (mm²) | Cable capacity Iz (A) | Ib ≤ In ≤ Iz | Longest run (m) | Voltage drop (V) | Voltage drop (%) | Voltage-drop check | Cable length estimate (m)
L1 | Bedrooms 1, 2 and 3 | 6 | 120 | 0.52174 | 6 | 1.5 | 13 | OK | 25 | 0.3913 | 0.1701% | OK | 45
L2 | Bathrooms 1 and 2, dressing room, entrance, sport room | 8 | 160 | 0.69565 | 6 | 1.5 | 13 | OK | 25 | 0.52174 | 0.2268% | OK | 55
L3 | Living room with open kitchen | 9 | 180 | 0.78261 | 6 | 1.5 | 13 | OK | 25 | 0.58696 | 0.2552% | OK | 45
Total |  | 23 | 460 | 2 | [8 empty] | 145
All lamps assigned to a circuit? |  | OK
Iz = 13 A is the lowest value for 1.5 mm² copper in Table 3 (conservative). Longest runs (25 m) and cable lengths (incl. ~10 % waste) are estimates from the plan: measure the wiring polylines in AutoCAD (LIST / LENGTH) and replace the yellow cells.

## Cost
Bill of quantities and cost estimate
Unit prices (yellow) are assumed market prices in USD – replace them with real prices.
No. | Item | Unit | Quantity | Unit price ($) | Amount ($)
1 | 20 W lamp, 2500 lm | pcs | 23 | 2 | 46
2 | One-way switch (single / double gang) | pcs | 9 | 1.2 | 10.8
3 | Junction box | pcs | 9 | 0.5 | 4.5
4 | Copper PVC cable 1.5 mm² | m | 145 | 0.35 | 50.75
5 | PVC conduit 20 mm | m | 120 | 0.3 | 36
6 | Distribution board, 6-way, with main switch / RCD | pcs | 1 | 25 | 25
7 | MCB 6 A | pcs | 3 | 3 | 9
8 | Accessories (clips, saddles, tape) | lot | 1 | 10 | 10
| Materials subtotal |  |  |  | 192.05
| Labour (% of materials) |  |  | 35% | 67.2175
| Subtotal |  |  |  | 259.2675
| Overhead and profit (% of subtotal) |  |  | 10% | 25.9267
| TOTAL ESTIMATED COST |  |  |  | 285.1943
Cable and conduit lengths are estimates (±10 %). Lamp price comes from the original report; all other prices, the labour % and the overhead % are assumptions.